## Blank
Site : | [5 empty] | Name of Auditor |  | Date of Audit
Item | Category | File | Description | Applicable Legislation | Compliance Evidence Required | Frequency | Compliant | Date of Inspection | Next Due Date | Rating | Comments of any findings | Action By? | Completed date
1 | F | 2 | Has the most recent fire risk assessment been completed and all actions completed | Regulatory Reform (Fire Safety) Order 2005. Approved Document B Volume 2 - Fire Safety: Building other than Dwelling Houses. BS1635:1990 | Risk Assessment Document | To define - Annual, Bi Annual or Tri Annual
2 | F | 2 | Have all the high and medium risk recommendations from the FRA been completed and signed off by appropriate parties? | Regulatory Reform (Fire Safety) Order 2005. Approved Document B Volume 2 - Fire Safety: Building other than Dwelling Houses. BS1635:1990 | Record Sheet | As per FRA timescale
3 | F | 2 | Are there records to confirm that the fire alarm and detection system been subject to a maintenance regime | Regulatory Reform (Fire Safety) Order 2005. BS9999. BS5839-1 | Certificate | Annually
4 | F | 2 | Is there an up to date fire log book in place | Regulatory Reform (Fire Safety) Order 2005. BS9999 | Log Book (Electronic Records are also acceptable) | Annually
4a | F | 2 | Have any remedial actions detailed within the log book been completed and signed off by appropriate parties. | Regulatory Reform (Fire Safety) Order 2005. BS9999 | Record Sheet | Annually
5 | F | 2 | Is there a testing regime to ensure weekly fire tests to ensure all fire alarm call points are tested over 12 months | Regulatory Reform (Fire Safety) Order 2005. BS9999. BS5839-1 | Record Sheet | Weekly
6 | F | 2 | Is there an up to date written suitable fire evacuation procedure ? | Regulatory Reform (Fire Safety) Order 2005. BS9999 | Procedure | Annually
7 | F | 2 | Is there an up-to-date record of periodic fire evacuation exercises (including false alarms) | Regulatory Reform (Fire Safety) Order 2005. BS9999 | Log | Annually
7a | F | 2 | Have any outstanding actions from evacuations exercises been rectified | Regulatory Reform (Fire Safety) Order 2005. BS9999 | Record Sheet | Not applicable
8 | F | 2 | Is there an up to date list of appointed fire wardens with names/contact details on display? | Regulatory Reform (Fire Safety) Order 2005. BS9999 | Log | Not applicable
9 | F | 2 | Is there a record to confirm that the wet/dry risers tests have been conducted within the last 12 months? | Regulatory Reform (Fire Safety) Order 2005. BS9999, BS9990:2008 | Record Sheet | Annually
10 | F | 2 | Is there a maintenance schedule in place for the inspection of fire appliances e.g. Portable Fire Extinguishers, Hose Reels and Fire Blankets | Regulatory Reform (Fire Safety) Order 2005. BS5306 Part 3, BS5306 Part 8, BSEN671-3, BS9999 | Record Sheet | Annually
11 | F | 2 | SELF TEST Units only. Is there recorded evidence of a maintenance schedule for emergency lighting testing to include Monthly Flick test Annual 3 hr discharge | BS EN 50172:2004, BS5266-8:2004; BS5266-1: 2016, BS9999:2008 | Certificate | Monthly
11.a | F | 2 | Have any identified deficiencies following Emergency lighting tests been rectified and signed off by appropriate parties? | BS EN 50172:2004, BS5266-8:2004; BS5266-1: 2016, BS9999:2008 | Record Sheet | Not applicable
11a1 | F | 2 | Central Battery Units Emergency Lighting System | BS EN 50172:2004, BS5266-8:2004; BS5266-1: 2016, BS9999:2008 | Record Sheet | 6 monthly (min)
12 | F | 2 | Is there recorded evidence that an up-to-date maintenance schedule in place for fire door hold open devices | Regulatory Reform (Fire Safety) Order 2005. BS5499:2013, BS8214 | Record Sheet | Annually
13 | F | 2 | Is there recorded evidence that an up-to-date maintenance schedule is in place for fire shutters/dampers | Regulatory Reform (Fire Safety) Order 2005. BS9999 | Record Sheet | Annually
13a | F | 2 | Have any deficiencies following fire damper maintenance been rectified and signed off by appropriate parties? | Regulatory Reform (Fire Safety) Order 2005. BS9999 | Record Sheet | Not applicable
14 | F | 2 | Is there recorded evidence that the fire signs have been checked on a monthly basis | Regulatory Reform (Fire Safety) Order 2005. BS9999 | Record Sheet | Monthly
14a | F | 2 | Have any deficiencies following fire signage checks been rectified? | Regulatory Reform (Fire Safety) Order 2005. BS9999 | Record Sheet | Monthly
15 | F | 2 | Is there recorded evidence that fire escape routes have been checked as clear on a weekly basis | Regulatory Reform (Fire Safety) Order 2005. BS9999 | Record Sheet | Weekly
15a | F | 2 | Have any deficiencies following escape route inspections been rectified? | Regulatory Reform (Fire Safety) Order 2005. BS9999 | Record Sheet | Weekly
16 | F | 2 | Have any deficiencies following external staircase inspections been rectified? | PUWER | Record Sheet | Not applicable
17 | F | 2 | Is there recorded evidence that lift phones have been checked on a monthly basis ? | MHSAWR 1999, Workplace Health, Safety and Welfare Regulations | Record Sheet | Monthly
17a | F | 2 | Have any deficiencies with Lift phones/phone lines been rectified? | MHSAWR 1999, Workplace Health, Safety and Welfare Regulations | Record Sheet | Monthly
18 | E | 1 | Is there a maintenance schedule and certificate in place for lightning protection? | BS EN 62305-3 / BS EN 62305-4 | Certificate | 11 Monthly
20 | W | 8 | Has a Water Safety Plan been devised ? |  | Procedure | Not applicable
21 | W | 8 | Has the WRA for this site been conducted in accordance with the assessed level of risk and does it include the following: A detailed scheme of management A written scheme of control | ACOP L8, HSG274 Parts 2 and 3 | Risk Assessment Document | 2-yearly maximum or when there is a change within 2 years
21a | W | 8 | Have all the high and medium risk recommendations from the WRA been completed and signed off by appropriate parties? | ACOP L8, HSG274 Parts 2 and 3 | Log | Not applicable
22 | W | 8 | Is there recorded evidence that a water temperature monitoring regime is in place to ensure hot water outlets remain above 55C, cold water outlets remain below 20C and TMV outlets are between 38C and 46C | ACOP L8, HSG274 Parts 2 and 3 | Record Sheet | Monthly
23 | W | 8 | Is there written up-to-date written evidence that storage Calorifier flow temperatures have been checked and confirmed to be within defined range. | ACOP L8, HSG274 Parts 2 and 3 | Record Sheet | Monthly
24 | W | 8 | Have any temperature monitoring deficiencies been rectified ? | ACOP L8, HSG274 Parts 2 and 3 | Record Sheet | Monthly
25 | W | 8 | Is there recorded evidence of TMV maintenance / testing in place for TMVs ? | ACOP L8, HSG274 Parts 2 and 3 | Record Sheet | Annually
25a | W | 8 | Have any TMV deficiencies been rectified ? | ACOP L8, HSG274 Parts 2 and 3, | Record Sheet | Not applicable
26 | W | 8 | Is there written up-to-date written evidence that all infrequently used outlets been flushed twice weekly? | ACOP L8, HSG274 Parts 2 and 3, | Record Sheet | Determined by WRA normally for health care twice weekly (See HTM 04-01 Part b)
27 | W | 8 | Where practical, is there up-to-date evidence that expansion vessels have been flushed. Note type (through flow expansion vessel or single entry) | ACOP L8, HSG274 Parts 2 and 3, | Record Sheet | As per Written Scheme
27a | W | 8 | Have any deficiencies with expansion vessel flushing needs been rectified | ACOP L8, HSG274 Parts 2 and 3 | Record Sheet
28 | W | 8 | Is there written up-to-date evidence that point of use filters have been installed / replaced as required | ACOP L8, HSG274 Parts 2 and 3 | Record Sheet | As required
29 | W | 8 | Is there written up-to-date that showers and spray taps have been dismantled, cleaned and descaled | ACOP L8, HSG274 Parts 2 and 3 | Record Sheet | 3-monthly
30 | W | 8 | Is there written up-to-date evidence that cold water storage tanks have been checked | ACOP L8, HSG274 Parts 2 and 3 | Record Sheet | Annually
30a | W | 8 | Have any deficiencies with cold water storage tanks been rectified | ACOP L8, HSG274 Parts 2 and 3 | Record Sheet
31 | W | 8 | Where appropriate is there written evidence that weekly dosing to water systems has taken place | ACOP L8, HSG274 Parts 2 and 3 | Record Sheet | Weekly
32 | W | 8 | Is there written up-to-date evidence that base exchange softeners have been serviced | ACOP L8, HSG274 Parts 2 and 3 | Record Sheet | Annually
33 | W | 8 | Is there written evidence that salt levels have been checked and maintained | ACOP L8, HSG274 Parts 2 and 3 | Record Sheet | Monthly
34 | W | 8 | Is there written evidence that point of use water heaters have been maintained | ACOP L8, HSG274 Parts 2 and 3 | Record Sheet | 6-Monthly
35 | W | 8 | Is there written evidence that water cooler/fountain drinking machines have been inspected, sanitised and had filters regularly changed. | ACOP L8, HSG274 Parts 2 and 3 | Record Sheet | 6-Monthly
36 | W | 8 | Is there written evidence of a water sampling and testing regime for pseudomonas aeruginosa been put in place | ACOP L8, HSG274 Parts 2 and 3 | Certificate | 6-Monthly or as recommended by WRA. Primary method of control is through Temperature
36a | W | 8 | have any recommendations from the water sampling regime been implemented | ACOP L8, HSG274 Parts 2 and 3 | Record Sheet | 6-Monthly or as recommended by WRA. Primary method of control is through Temperature
37 | E | 1 | Is there written up-to-date written evidence that LV Electrical System Test & Inspection have been conducted | EAWR 89, BS7671:2008 (2015), IET GN3 | Certificate | As per BS:7671 Regulations
37a | E | 1 | Have all Category 1 deficiencies rectified ? | EAWR 89, BS7671:2008 (2015), IET GN3 | Record Sheet | As per BS:7671 Regulations
37b | E | 1 | Have all Category 2 deficiencies rectified ? | EAWR 89, BS7671:2008 (2015), IET GN3 | Record Sheet | As per BS:7671 Regulations
38 | E | 1 | Is there written up-to-date written evidence that Distribution Board (DB) Inspections have been conducted (Thermal Imaging?) | EAWR 89, BS7671:2008 (2015), IET GN3 | Record Sheet | Annually
39 | E | 1 | Is there written up-to-date written evidence that generators (including CHP units) have been maintained? | PUWER, EAWR 89 | Record Sheet | Annually
39a | E | 1 | Have any generator / CHP deficiencies been rectified | PUWER, EAWR 89 | Record Sheet | not applicable
39b | E | 1 | Has a black start or True Load test been completed? | PUWER, EAWR 89 | Record Sheet | Annually
40 | E | 1 | Is there written up-to-date written evidence that Uninterruptable Power Supplies (UPS) have been maintained ? | PUWER, EAWR 89 | Record Sheet | 6-Monthly
40a | E | 1 | Have any deficiencies regarding UPS installations been rectified | PUWER, EAWR 89 | Record Sheet | As applicable
41 | E | 1 | Is there written up-to-date evidence that all portable electrical appliances have been tested? | EAWR 89, HSG107 | Certificate | Frequency as per IEE Code of Practice
42 | E | 1 | Is there written up-to-date written evidence that Residual Current Devices have been tested that details trip time and fault current? | EAWR 89, BS7671:2008 (2015) Regulations 612, 510.3 | Certificate | Annual
42a | E | 1 | Are RCD's being tested quarterly. (Functional Test). | EAWR 89, BS7671:2008 (2015) Regulations 612, 510.3 | Record Sheet | 3 monthly
43 | F | 2 | Is there written up-to-date written evidence that CCTV equipment has been maintained with any deficiencies rectified within an appropriate timescale? | GDPR | Maintenance Records / only authorised users to view | 6-Monthly
43a | F | 2 | Have any deficiencies with the CCTV system been rectified | GDPR | Maintenance Records / only authorised users to view | Not applicable
44 | F | 2 | Is there written up-to-date written evidence that Intruder Alarm equipment has been maintained with any deficiencies rectified within an appropriate timescale? | Insurance Requirement | Record Sheet | 6-Monthly
44a | F | 2 | Have any deficiencies with the Intruder Alarm System been rectified | Insurance Requirement | Record Sheet | Not applicable
45 | F | 2 | Is there written up-to-date written evidence that Access Control equipment has been maintained with any deficiencies rectified within an appropriate timescale? | Insurance Requirement | Record Sheet | 6-Monthly
45a | F | 2 | Have any deficiencies with the Access Control System been rectified | Insurance Requirement | Record Sheet | Not applicable
46 | F | 2 | Is there written up-to-date written evidence that installed (not portable) Hearing Loop Induction equipment has been maintained | EA 2010 | Record Sheet | Annually
48 | F | 2 | Is there written evidence that Disabled WC Call Alarm System equipment has been tested ? | EA 2010 | Record Sheet | Monthly
48a | F | 2 | Have any deficiencies with the Disabled WC Alarm System been rectified | EA 2010 | Record Sheet | Not applicable
49 | E | 1 | Is there written evidence that radiation leakage tests have been undertaken on commercial grade microwave ovens | EAWR 89, HSG107 | Certificate | Annually
50 | G | 3 | Is there up-to-date written evidence that Gas Pipework Tightness testing has taken place | GSIUR1998 (ACOP L56) | Certificate | In accordance with Clause 4.2 and Figure 4 of IGE/UP/1A Edition 2
51 | G | 3 | Is there up-to-date written evidence that LPG Pipework, Tank testing & Inspection has taken place | GSIUR1998 (ACOP L56) | Certificate | Annually
52 | G | 3 | Have any deficiencies with the LPG System been rectified | GSIUR1998 (ACOP L56) | Certificate | Not applicable
53 | G | 3 | Is there up-to-date written evidence that Boilers/ Gas Water Heater Servicing has taken place ? | GSIUR1998 (ACOP L56) | Certificate | Annually or as indicated by Manufacturers Instructions
53a | G | 3 | Have any deficiencies with the Boilers / gas water heaters been rectified | GSIUR1998 (ACOP L56) | Certificate | Not applicable
54 | G | 3 | Is there up-to-date written evidence that Gas catering equipment maintenance & testing has taken place | GSIUR1998 (ACOP L56), BS6173:2009 | Certificate | Annually
55 | P | 6 | Is there up-to-date written evidence that pressure systems inspections have taken place | PSSR 2000, BS7074-2, PSG4, L122 | Statutory inspection by Allianz (or other competent person) for systems within PSSR threshold. For systems under the PSSR threshold, record sheet. | As per Written Scheme. PSSR require qualifying liquids over 250 bar litre, for MTHW, HTHW or refrigeration systems over 25kW
56 | P | 6 | Is there written up-to-date evidence that storage Calorifiers have been inspected internally ? | ACOP L8, HSG274 Parts 2 and 3 | Record Sheet | Annually
57 | L | 4 | Is there an inventory of equipment that falls under the Lifting Operations & Lifting Equipment Regulations, for the site? | LOLER | Record Sheet | Annually
58 | L | 4 | Is there written evidence that passenger lift have been maintained and certified | LOLER | Statutory inspection by Allianz (or other competent person) | 6 monthly (min)
58a | L | 4 | Have any deficiencies with the lift installations been rectified | LOLER | Record Sheet | As required
59 | L | 4 | Is there up-to-date written evidence that hoists have been maintained and certified | LOLER | Statutory inspection by Allianz (or other competent person) | 6-Monthly
60 | L | 4 | Is there written evidence that man safe / latch way and eyebolt systems have been maintained and certified | PUWER | Certificate | Annually
61 | L | 4 | Is there written evidence that cradle systems have been maintained and certified | LOLER | Statutory inspection by Allianz (or other competent person) | 3 & 6 Monthly
62 | L | 4 | Is there written evidence that lifting beams inspections have taken place | LOLER | Statutory inspection by Allianz (or other competent person) | Annually
63 | L | 4 | Is there up-to-date written evidence that portable ladder inspections have taken place | PUWER, MHSAWR, WAHR | Scoff Tag | 6-Monthly
64 | L | 4 | Is there up-to-date written evidence that portable scaffold inspections have taken place | PUWER, MHSAWR, WAHR | Scaff Tag | 6-Monthly
65 | V | 6 | Is there up-to-date written evidence that LEV maintenance has taken place with any deficiencies rectified within an appropriate timescale? | HSG258 | Certificate and maintenance records | Annually
66 | V | 6 | Is there up-to-date written evidence that fume cupboard maintenance has taken place ? | HSG258 | Certificate and maintenance records | Annually
67 | V | 8 | Is there up-to-date written evidence that petrol interceptor maintenance has taken place | PPG3, BSEN 858 | Record Sheet | Annually
68 | V | 7 | Is there up-to-date written evidence that Oil/ Diesel Tank Inspections have taken place ? | DSEAR | Record Sheet, and DSEAR risk assessment | Annually. Is there a DSEAR risk assessment in place?
69 | V | 6 | Is there written evidence that A/C Systems F-Gas leak tests have been undertaken for applications producing between 5 - 50 Tonnes CO2e (Typically system containing up to 3Kg) | The Flourinated Greenhouse Gases Regulations (EU)517 2014. The Ozone Depleting Substances (Qualifications) Regulations 2006 | Record Sheet | Annually
70 | V | 6 | Is there written evidence that A/C Systems F-Gas leak tests have been undertaken for applications producing between 50 - 500 Tonnes CO2e (Typically containing up to 30 kg ) | The Flourinated Greenhouse Gases Regulations (EU)517 2014. The Ozone Depleting Substances (Qualifications) Regulations 2006 | Record Sheet | 6-Monthly
71 | V | 6 | Is there an automatic Refrigerant Leak Detection system insulted on A/C Systems F-Gas leak tests have been undertaken for applications Producing more than 500 Tonnes CO2e, and has this been checked on the last Chiller Service? (Above 30Kg) | The Flourinated Greenhouse Gases Regulations (EU)517 2014. The Ozone Depleting Substances (Qualifications) Regulations 2006 | Record Sheet | 6-Monthly
72 | V | 6 | Is there written evidence that energy audits have been undertaken on air condition systems rated over 12kW. Note this is 12kW for comfort heating / cooling only and not include any process cooling e.g. for server rooms. | Energy Performance of Buildings (Certificates and Inspections) (England and Wales) Regulations | Certificate | 5-yearly
73 | V | 6 | Have any deficiencies with any air conditioning system within the building been rectified | The Flourinated Greenhouse Gases Regulations (EU)517 2014. The Ozone Depleting Substances (Qualifications) Regulations 2006 | Record Sheet | 3-monthly
74 | En | 7 | Is there a Display Energy Certificate on display? | England and Wales of the European Directives 2002/91/EC and 2010/31/EU on the Energy performance of buildings. | Certificate | Annually
75 | En | 7 | Is there an Energy Performance Report. | England and Wales of the European Directives 2002/91/EC and 2010/31/EU on the Energy performance of buildings | Recommendations Report | 10 Year
76 | M | 6 | Is there up-to-date written evidence that kitchen areas have been subject to a deep clean? | PUWER | Record Sheet | Annually
77 | M | 6 | Is there up-to-date written evidence that kitchen ductwork have been subject to annual cleaning? | TR19 | Certificate | Annually (or more frequently depending on use)
78 | M | 6 | Is there up-to-date written evidence that kitchen grease traps have been subject to monthly cleaning? | PPG3, BS 12056-5, BS 1825-2 | Record Sheet | Monthly
79 | PUWER | 9 | Is there up-to-date written evidence that automatic door maintenance has taken place with any deficiencies rectified within an appropriate timescale? | ACOP L24 Regulation 5, Regulation 18. Supply of Machinery (Safety) Regulations 2008. BS 7036-0: 2014. BS EN 16005:2012 | Record Sheet | 6-Monthly
80 | PUWER | 9 | Is there up-to-date written evidence that folding wall maintenance has taken place. | PUWER | Record Sheet | Annually
81 | WORKPLACE | 10 | Is there up-to-date written evidence that gym equipment maintenance has taken place | PUWER | Record Sheet | Annually
82 | M | 9 | Is there up-to-date written evidence that x-ray equipment Radiation leakage tests have taken place | PUWER | Record Sheet | Annual
84 | M | 6 | Have all recommendations from the medical gas audits been completed | PUWER | Record Sheet | Quarterly
85 | As | 5 | Is there an asbestos survey and asbestos management plan confirming condition based inspections have been undertaken | Control of Asbestos Regulations 2012 (L143) | Asbestos Survey and Management Plan | Annual
86 | M | 6 | Have all ventilation systems had an duct cleanliness inspection? | TR19 | Sample Results and cleaning records (if necessary) | Annual or less frequently depending on risk.
87 | F | 2 | Is there an annual Fire Stopping Inspection? | Regulatory Reform (Fire Safety) Order 2005 Building Regulations Approved Document B ISBN87040919 | Record Sheet | Annual
Key:
Fire | F
Water | W
Electricity | E
Gas | G
Pressure | P
Lifts | L
Ventilation | A
Environment | En
Miscellaneou | M
Asbestos | As